{"text_format":"3","workbook":"xls","n_sheets":11,"sheets":["扉-2_招标控制价","表-01_总说明","表-03_单项工程招标控制价汇总表","表-04_单位工程招标控制价汇总表","表-08_分部分项工程和单价措施项目清单与计价表","表-09_工程量清单综合单价分析表(主材)","表-11_总价措施项目清单与计价表","表-14_税前项目清单与计价表","表-15_规费、增值税计价表","主要材料及价格表(有信息价)","设备及价格表"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"扉-2_招标控制价","index":0,"n_rows":46,"n_cols":9,"rows_kept":46,"merged":[[1,1,1,6],[5,1,5,7],[11,0,11,1],[11,3,11,7],[13,3,14,7],[18,2,19,4],[18,6,19,8],[19,0,19,1],[20,2,20,4],[20,6,20,8],[24,0,24,1],[24,2,25,4],[24,6,25,8],[25,0,25,1],[26,2,26,4],[26,6,26,8],[30,2,31,4],[30,6,31,8],[31,0,31,1],[32,2,32,4],[32,6,32,8],[37,0,37,1],[37,2,37,4],[37,6,37,8],[42,2,42,6]],"flags":["formulas_cached_only"]}
[]
[null,"中国—东盟传统医药文化交流中心配电工程",{"$nulls":5},"工程"]
[]
[]
[]
[null,"招 标 控 制 价"]
[]
[]
[]
[]
[]
["  招标控制价",null,"(小写):","1572585.27元"]
[]
[{"$nulls":3},"壹佰伍拾柒万贰仟伍佰捌拾伍元贰角柒分"]
[null,null,"(大写):"]
[]
[]
[]
[{"$nulls":5},"工程造价  "]
["  招  标  人:",{"$nulls":4},"咨 询 人："]
[null,null,"（单位盖章）",{"$nulls":3},"（单位资质专用章）"]
[]
[]
[]
["  法定代表人 ",{"$nulls":4},"法定代表人  "]
["或其授权人：",{"$nulls":4},"或其授权人："]
[null,null,"（签字或盖章）",{"$nulls":3},"（签字或盖章）"]
[]
[]
[]
[]
["编  制  人：",{"$nulls":4},"复  核  人："]
["                 ",null,"（造价人员签字）",{"$nulls":3},"(造价工程师签字盖专用章)"]
[]
[]
[]
[]
["  编 制 时 间:",null,"2021年09月09日",null,null,"复 核 时 间：","2021年09月09日"]
{"$rows_empty":7}
[{"$nulls":8},"扉-2"]

{"sheet":"表-01_总说明","index":1,"n_rows":38,"n_cols":3,"rows_kept":38,"merged":[[0,0,0,2],[2,0,36,2]],"flags":["formulas_cached_only"]}
["总  说  明"]
["工程名称:","中国—东盟传统医药文化交流中心配电工程","第1页 共1页"]
["    一、工程概况：本工程建设地点位于广西南宁市广西中医药大学(仙葫小区)，属于新建10KV配电工程，主要工作内容有室外高压线管敷设、地下室配电房高低压柜、2台1000KVA变压器、配电房基础及装修，其余内容详见预算书。\r\n    \r\n    二、编制依据：\r\n    1、设计图纸、图集、规范及现场实际情况；\r\n    2、《建设工程工程量清单计价规范》（GB 50500-2013）及广西壮族自治区实施细则、GB50854～50862-2013《建设工程工程量清单计算规范广西壮族自治区实施细则》（修订本）。\r\n    3、广西壮族自治区建设行政主管部门颁发的2013年《广西壮族自治区建筑装饰装修工程消耗量定额》、2015年《广西壮族自治区安装工程消耗量定额》、2014年《广西壮族自治区市政工程消耗量定额》。\r\n    4、2016年《广西壮族自治区建设工程费用定额》。\r\n    5、《关于调整建设工程定额人工费及有关费率的通知》（桂建标[2018]19号）。\r\n    6、《关于建筑业实施营业税改增值税后广西壮族自治区建设工程计价依据调整的通知》桂建标[2016]17号、《关于营改增后价格信息发布工作调整的通知》桂造价[2016]7号。\r\n    7、《关于调整除税价计算适用增值税 税率的通知》桂造价[2018]14号。\r\n    8、《自治区住房城乡建设厅关于调整建设工程计价增值税税率的通知》桂建标[2019]12号。\r\n    9、材料价格按《南宁建设工程造价信息》2021年第8期上半月信息价，南宁市信息价没有刊登的价格，参照市场询价综合考虑取定。\r\n\r\n    四、其他说明：\r\n    1、该工程采用一般计税方法计算，增值税按9%计取，相关费率有区间值的按中间值计取。\r\n    2、该工程土壤类别暂按三类土计算，弃土运距暂按10公里计算。\r\n    3、预算不含配电房墙体砌筑、只包含配电房基础、防火门、墙及天棚装饰。\r\n    4、图纸缺少室外管沟及检查井大样，暂参考《南方电网10KV和35KV配电标准设计》做法计算。\r\n    5、预算已经计算地下室暗室施工增加费。"]
{"$rows_empty":34}
[null,"表-01"]

{"sheet":"表-03_单项工程招标控制价汇总表","index":2,"n_rows":35,"n_cols":5,"rows_kept":35,"merged":[[0,0,0,4],[1,0,1,3],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,2,4],[3,3,4,3]],"flags":["formulas_cached_only"]}
["单项工程招标控制价汇总表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程",{"$nulls":3},"第1页 共1页"]
["序号","单位工程名称","金额(元)","其中:(元)"]
[{"$nulls":3},"暂估价","安全文明"]
[{"$nulls":4},"施工费"]
["1.1","中国—东盟传统医药文化交流中心配电工程-安装工程",1475980.53,null,7153.22]
["1.2","中国—东盟传统医药文化交流中心配电工程-土建工程",79271.23,null,3969.65]
["1.3","中国—东盟传统医药文化交流中心配电工程-市政工程",17333.51,null,379.86]
[null,"        招标控制价合计",1572585.27,null,11502.73]
{"$rows_empty":25}
[{"$nulls":4},"表-03"]

{"sheet":"表-04_单位工程招标控制价汇总表","index":3,"n_rows":84,"n_cols":4,"rows_kept":84,"merged":[[0,0,0,3],[1,0,1,2],[42,0,42,3],[43,0,43,2]],"flags":["formulas_cached_only"]}
["单位工程招标控制价汇总表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程",null,null,"第1页 共2页"]
["序号","汇总内容","金额(元)","备注"]
[null,"中国—东盟传统医药文化交流中心配电工程-安装工程"]
["1","分部分项工程和单价措施项目清单计价合计",1316716.71]
[" 1.1","  其中:暂估价"]
["2","总价措施项目清单计价合计",22026.36]
[" 2.1","  其中:安全文明施工费",7153.22]
["3","其他项目清单计价合计"]
["4","税前项目清单计价合计"]
["5","规费",15367.51]
["6","增值税",121869.95]
["7","工程总造价=1+2+3+4+5+6",1475980.53]
[null,"中国—东盟传统医药文化交流中心配电工程-土建工程"]
["1","分部分项工程和单价措施项目清单计价合计",59481.88]
[" 1.1","  其中:暂估价"]
["2","总价措施项目清单计价合计",6653.59]
[" 2.1","  其中:安全文明施工费",3969.65]
["3","其他项目清单计价合计"]
["4","税前项目清单计价合计",{"v":2529,"d":"2529.00"}]
["5","规费",4061.43]
["6","增值税",6545.33]
["7","工程总造价=1+2+3+4+5+6",79271.23]
[null,"中国—东盟传统医药文化交流中心配电工程-市政工程"]
["1","分部分项工程和单价措施项目清单计价合计",15034.68]
[" 1.1","  其中:暂估价"]
["2","总价措施项目清单计价合计",501.16]
[" 2.1","  其中:安全文明施工费",379.86]
["3","其他项目清单计价合计"]
["4","税前项目清单计价合计"]
["5","规费",366.46]
["6","增值税",1431.21]
["7","工程总造价=1+2+3+4+5+6",17333.51]
[null,"工程项目汇总"]
["1","分部分项工程和单价措施项目清单计价合计",1391233.27]
["1.1","  其中:暂估价"]
["2","总价措施项目清单计价合计",29181.11]
["2.1","  其中:安全文明施工费",11502.73]
["3","其他项目清单计价合计"]
["4","税前项目清单计价合计",{"v":2529,"d":"2529.00"}]
["5","规费",{"v":19795.4,"d":"19795.40"}]
[null,null," ","表-04"]
["单位工程招标控制价汇总表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程",null,null,"第2页 共2页"]
["序号","汇总内容","金额(元)","备注"]
["6","增值税",129846.49]
["7","工程总造价=1+2+3+4+5+6",1572585.27]
{"$rows_empty":36}
[null,null," ","表-04"]

{"sheet":"表-08_分部分项工程和单价措施项目清单与计价表","index":4,"n_rows":345,"n_cols":8,"rows_kept":345,"merged":[[0,0,0,7],[1,0,1,5],[1,6,1,7],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,4,4,4],[2,5,2,7],[3,5,4,5],[3,6,4,6],[36,0,36,7],[37,0,37,5],[37,6,37,7],[38,0,40,0],[38,1,40,1],[38,2,40,2],[38,3,40,3],[38,4,40,4],[38,5,38,7],[39,5,40,5],[39,6,40,6],[73,0,73,7],[74,0,74,5],[74,6,74,7],[75,0,77,0],[75,1,77,1],[75,2,77,2],[75,3,77,3],[75,4,77,4],[75,5,75,7],[76,5,77,5],[76,6,77,6],[109,0,109,7],[110,0,110,5],[110,6,110,7],[111,0,113,0],[111,1,113,1],[111,2,113,2],[111,3,113,3],[111,4,113,4],[111,5,111,7],[112,5,113,5],[112,6,113,6],[145,0,145,7],[146,0,146,5],[146,6,146,7],[147,0,149,0],[147,1,149,1],[147,2,149,2],[147,3,149,3],[147,4,149,4],[147,5,147,7],[148,5,149,5],[148,6,149,6],[184,0,184,7],[185,0,185,5],[185,6,185,7],[186,0,188,0],[186,1,188,1],[186,2,188,2],[186,3,188,3],[186,4,188,4],[186,5,186,7],[187,5,188,5],[187,6,188,6],[220,0,220,7],[221,0,221,5],[221,6,221,7],[222,0,224,0],[222,1,224,1],[222,2,224,2],[222,3,224,3],[222,4,224,4],[222,5,222,7],[223,5,224,5],[223,6,224,6],[261,0,261,7],[262,0,262,5],[262,6,262,7],[263,0,265,0],[263,1,265,1],[263,2,265,2],[263,3,265,3],[263,4,265,4],[263,5,263,7],[264,5,265,5],[264,6,265,6],[302,0,302,7],[303,0,303,5],[303,6,303,7],[304,0,306,0],[304,1,306,1],[304,2,306,2],[304,3,306,3],[304,4,306,4],[304,5,304,7],[305,5,306,5],[305,6,306,6]],"flags":["formulas_cached_only"]}
["分部分项工程和单价措施项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":5},"第1页 共9页"]
["序\r\n\r\n号","项目编码","项目名称及\r\n项目特征描述","计量单位","工程量","金额(元)"]
[{"$nulls":5},"综合单价","合 价","其中："]
[{"$nulls":7},"暂估价"]
[null,null,"中国—东盟传统医药文化交流中心配电工程-安装工程",{"$nulls":3},1316716.71]
[null,null,"分部分项工程",{"$nulls":3},1316716.71]
[null,null,"B4 电气设备安装工程（高低压系统）",{"$nulls":3},{"v":1289817.3,"d":"1289817.30"}]
["1","030401002001","干式变压器 SCB13-1000KVA","台","2",126863.17,253726.34]
[null,null,"1.规格：SCB13-1000KVA，D,yn11 Uk=6%；"]
[null,null,"2.高压调节范围：10.5±2*2.5%/0.4KV；"]
[null,null,"3.带风机、温显温控系统、IP31外壳；"]
[null,null,"4.变压器噪音水平应低于：白昼55dB(A)、夜间45dB(A)；"]
[null,null,"5.变压器应符合入网要求、品牌相当于“ABB”或者“施奈德”"]
["2","030402017001","高压成套配电柜 进线柜AH1","台","1",77681.89,77681.89]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“南宁乔顿”"]
["3","030402017002","高压成套配电柜 出线柜AH2","台","1",75615.34,75615.34]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“南宁乔顿”"]
["4","030402017003","高压成套配电柜 出线柜AH3","台","1",75615.34,75615.34]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“南宁乔顿”"]
["5","030404004001","低压开关柜 进线柜1AA1","台","1",65257.34,65257.34]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["6","030404009001","低压电容器柜 补偿柜1AA2","台","1",61603.41,61603.41]
[{"$nulls":7},"表-08"]
["分部分项工程和单价措施项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":5},"第2页 共9页"]
["序\r\n\r\n号","项目编码","项目名称及\r\n项目特征描述","计量单位","工程量","金额(元)"]
[{"$nulls":5},"综合单价","合 价","其中："]
[{"$nulls":7},"暂估价"]
[null,null,"1.规格:800*1000*2200mm；380V 300kvar"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["7","030404004002","低压开关柜 出线柜1AA3","台","1",29356.63,29356.63]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["8","030404004003","低压开关柜 出线柜1AA4","台","1",29694.86,29694.86]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["9","030404004004","低压开关柜 出线柜1AA5","台","1",30098.13,30098.13]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["10","030404004005","低压开关柜 出线柜1AA6","台","1",31595.08,31595.08]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["11","030404004006","低压开关柜 进线柜2AA1","台","1",65257.34,65257.34]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体底部及孔洞防火封堵做法详见图纸；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["12","030404009002","低压电容器柜 补偿柜2AA2","台","1",61603.41,61603.41]
[null,null,"1.规格:800*1000*2200mm；380V 300kvar"]
[{"$nulls":7},"表-08"]
["分部分项工程和单价措施项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":5},"第3页 共9页"]
["序\r\n\r\n号","项目编码","项目名称及\r\n项目特征描述","计量单位","工程量","金额(元)"]
[{"$nulls":5},"综合单价","合 价","其中："]
[{"$nulls":7},"暂估价"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["13","030404004007","低压开关柜 联络柜2AA3","台","1",59775.04,59775.04]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["14","030404004008","低压开关柜 出线柜2AA4","台","1",30254.24,30254.24]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["15","030404004009","低压开关柜 出线柜2AA5","台","1",35590.66,35590.66]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["16","030404004010","低压开关柜 出线柜2AA6","台","1",31813.44,31813.44]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
["17","030414007001","在线式不间断电源 UPS-2KVA","套","1",3293.84,3293.84]
["18","030403003001","带形铜母线安装 TMY-80*8mm2","m","32.20",519.64,16732.41]
[null,null,"1.含母线绝缘支架、热缩管及其他配件。"]
["19","030403003002","带形铜母线安装 TMY-100*10mm2","m","16.00",780.97,12495.52]
[null,null,"1.含母线绝缘支架、热缩管及其他配件。"]
["20","030403003003","带形铜母线引下线 带形母线 TMY-80*8mm2","m","4.00",539.58,2158.32]
[null,null,"1.含母线绝缘支架、热缩管及其他配件。"]
[{"$nulls":7},"表-08"]
["分部分项工程和单价措施项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":5},"第4页 共9页"]
["序\r\n\r\n号","项目编码","项目名称及\r\n项目特征描述","计量单位","工程量","金额(元)"]
[{"$nulls":5},"综合单价","合 价","其中："]
[{"$nulls":7},"暂估价"]
["21","030403003004","带形铜母线引下线 带形母线 TMY-100*10mm2","m","8.00",803.41,6427.28]
[null,null,"1.含母线绝缘支架、热缩管及其他配件。"]
["22","030403006001","低压封闭式插接母线槽 2000A/4P","m","11.50",3290.99,37846.39]
[null,null,"1.部位：TM1到1AA1、TM2到2AA1、2AA3到1AA3；"]
[null,null,"2.含弯头、连接器、支架及其他配件，母线终端箱另计。"]
[null,null,"3.符合入网要求、品牌相当于或优于“广西派丰”。"]
["23","030403007001","母线终端箱 2000A/4P","台","6",956.34,5738.04]
[null,null,"1.部位：TM1到1AA1、TM2到2AA1、2AA3到1AA3；"]
[null,null,"2.含变压器低压母线连接、低压柜母线连接及其他配件。"]
["24","030408001001","铜芯电力电缆 ZR-YJV22-8.7/15KV-3*120mm2","m","280.00",364.73,{"v":102124.4,"d":"102124.40"}]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
["25","030408001002","铜芯电力电缆 ZR-YJV22-8.7/15KV-3*70mm2","m","38.70",{"v":232.2,"d":"232.20"},8986.14]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
["26","030408001003","铜芯电力电缆 ZR-VV-0.6/1KV-120mm2","m","10.00",84.88,{"v":848.8,"d":"848.80"}]
[null,null,"1.用于变压器连接低压柜PE接用；"]
[null,null,"2.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
["27","030408006001","户内10KV冷缩电力电缆头制作、安装 70mm2","个","4",644.19,2576.76]
["28","030408006002","户内10KV冷缩电力电缆头制作、安装 120mm2","个","2",886.32,1772.64]
["29","桂030404039001","焊、压铜接线端子 120mm2","个","4",27.15,{"v":108.6,"d":"108.60"}]
["30","030408003001","电缆保护管 C-PVC-167*8.5","m","144.40",73.66,{"v":10636.5,"d":"10636.50"}]
[null,null,"1.含管枕、配件，管沟土方挖填另计。"]
[null,null,"2.品牌相当于或优于“雄塑”、“联塑”。"]
["31","030411003001","电缆桥架 200*150*2.0mm","m","60.00",115.94,{"v":6956.4,"d":"6956.40"}]
[null,null,"1.含盖板、弯头、三通、配件、接地线，支架及刷油另计。"]
[null,null,"2.品牌相当于或优于“南宁乔顿”、“北乔”。"]
["32","030408008001","高低压配电柜内壁防火堵洞","处","44",93.03,4093.32]
[null,null,"按设计说明施工"]
["33","030408009001","高低压配电柜内壁防火隔板","㎡","11.08",209.18,2317.71]
[null,null,"按设计说明施工"]
["34","030408010001","高低压配电柜内壁防火涂料","kg","8.20",24.63,201.97]
[{"$nulls":7},"表-08"]
["分部分项工程和单价措施项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":5},"第5页 共9页"]
["序\r\n\r\n号","项目编码","项目名称及\r\n项目特征描述","计量单位","工程量","金额(元)"]
[{"$nulls":5},"综合单价","合 价","其中："]
[{"$nulls":7},"暂估价"]
[null,null,"按设计说明施工"]
["35","030408008002","电缆桥架穿墙体防火封堵","处","5",435.25,2176.25]
[null,null,"1.做法详见图纸。"]
["36","030413001001","桥架支架制作、安装","kg","108.99",17.72,{"v":1931.3,"d":"1931.30"}]
[null,null,"1.支架采用角钢，除锈、刷油另计。"]
[null,null,"2.按设计图纸施工(HX-P19035ZBS-AO 1-35)。"]
["37","030413001002","电缆支架","kg","223.94",18.78,4205.59]
[null,null,"1.L50*5热镀锌角钢加工，每@800mm预埋一组支架，一组3层。"]
["38","031201003001","金属结构刷油","kg","108.99",2.61,284.46]
[null,null,"1.手工除锈，刷防锈漆、调和漆各两道。"]
["39","030414001001","电力变压器系统调试 10KV以下(容量2000KV.A以下)","系统","2",7538.37,15076.74]
["40","030414002001","送配电装置系统调试 1KV以下交流供电","系统","9",{"v":1206.9,"d":"1206.90"},{"v":10862.1,"d":"10862.10"}]
["41","030414002002","送配电装置系统调试 10KV以下交流供电","系统","2",1952.74,3905.48]
["42","030414004001","自动投入装置调试  备用电源自投装置","系统","1",1432.62,1432.62]
["43","030414008001","母线调试 母线系统 1KV以下","段","3",535.88,1607.64]
["44","030414008002","母线调试 母线系统 10KV以下","段","1",1977.72,1977.72]
["45","030414009001","避雷器调试 1KV以下","组","4",560.07,2240.28]
["46","030414009002","避雷器调试 10KV以下","组","1",1017.31,1017.31]
["47","030414010001","电容器调试 1KV以下","组","2",456.53,913.06]
["48","030414015001","电缆试验 泄露试验","根","3",186.75,560.25]
["49","030414015002","电缆试验 交流耐压试验","根","3",590.99,1772.97]
[null,null,"B4 电气设备安装工程（配电房照明）",{"$nulls":3},{"v":26242.8,"d":"26242.80"}]
["50","030404017001","室内照明配电箱","台","1",{"v":625.4,"d":"625.40"},{"v":625.4,"d":"625.40"}]
[null,null,"1.304不锈钢材质；"]
[null,null,"2.安装方式:底边距地1.3米暗装；"]
[null,null,"3.内部元件详见图纸系统图；"]
[null,null,"4.箱内元件品牌相当于或优于“ABB”、“施耐德”。"]
["51","030404034001","双极双控开关 20A 220V","套","2",{"v":26,"d":"26.00"},{"v":52,"d":"52.00"}]
[null,null,"1.安装方式:底边距地1.3米暗装。"]
[null,null,"2.品牌相当于或优于“TCL”、“西蒙”。"]
["52","030404035001","两孔三孔暗插座 16A 220V","套","8",27.43,219.44]
[null,null,"1.安装方式:底边距地0.3米暗装。"]
[null,null,"2.品牌相当于或优于“TCL”、“西蒙”。"]
[{"$nulls":7},"表-08"]
["分部分项工程和单价措施项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":5},"第6页 共9页"]
["序\r\n\r\n号","项目编码","项目名称及\r\n项目特征描述","计量单位","工程量","金额(元)"]
[{"$nulls":5},"综合单价","合 价","其中："]
[{"$nulls":7},"暂估价"]
["53","030412005001","双管普通日光灯 2*24W","套","18",82.29,1481.22]
[null,null,"1.安装方式:吸顶安装。"]
[null,null,"2.品牌相当于或优于“三雄极光”、“欧普”。"]
["54","030412004001","安全出口标志","套","1",91.69,91.69]
[null,null,"1.安装方式:门框上方0.2米壁装。"]
[null,null,"2.品牌相当于或优于“广威消防”、“安尔顿照明”。"]
["55","030412004002","单向疏散灯","套","6",101.79,610.74]
[null,null,"1.安装方式:距地0.3米壁装。"]
[null,null,"2.品牌相当于或优于“广威消防”、“安尔顿照明”。"]
["56","030108003001","轴流风机 160W","台","4",1074.92,4299.68]
[null,null,"1.含2个进风防火阀，2个排风防火阀及配电房门防鼠网；"]
[null,null,"2.安装方式:距地3.5米壁装。"]
[null,null,"3.品牌相当于或优于“美的”、“金羚”。"]
["57","030408001004","铜芯电力电缆 WDZN-YJV-0.6/1KV-4*25mm2","m","50.00",{"v":105.2,"d":"105.20"},{"v":5260,"d":"5260.00"}]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
["58","030411004001","管内穿线 照明线路 NH-BV-0.4/1KV-2.5mm2","m","600.00",{"v":3.3,"d":"3.30"},{"v":1980,"d":"1980.00"}]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
["59","030411004002","管内穿线 动力线路 NH-BV-0.4/1KV-4mm2","m","300.00",4.44,{"v":1332,"d":"1332.00"}]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
["60","030411004003","管内穿线 动力线路 NH-BV-0.4/1KV-6mm2","m","300.00",6.22,{"v":1866,"d":"1866.00"}]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
["61","030411001001","砖、混凝土结构暗配 KBG可挠金属管 φ16","m","400.00",10.68,{"v":4272,"d":"4272.00"}]
[null,null,"品牌相当于或优于“雄塑”、“联塑”。"]
["62","030409001001","接地极 L50*5热镀锌角钢 L=2.5M","根","12",{"v":115.9,"d":"115.90"},{"v":1390.8,"d":"1390.80"}]
[null,null,"1.部位：室外管沟内。"]
["63","030409002001","户内接地母线 -50*5热镀锌扁钢","m","92.06",26.36,{"v":2426.7,"d":"2426.70"}]
[null,null,"1.部位：配电房内。"]
["64","030414011001","接地装置调试  独立接地装置","系统","1",335.13,335.13]
[null,null,"B9 给排水、燃气工程",{"$nulls":3},656.61]
["65","030901013001","灭火器及箱体","套","3",218.87,656.61]
[{"$nulls":7},"表-08"]
["分部分项工程和单价措施项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":5},"第7页 共9页"]
["序\r\n\r\n号","项目编码","项目名称及\r\n项目特征描述","计量单位","工程量","金额(元)"]
[{"$nulls":5},"综合单价","合 价","其中："]
[{"$nulls":7},"暂估价"]
[null,null,"1.箱体规格:600*100*800mm；"]
[null,null,"2.内含两具灭火器。"]
[null,null,"3.品牌相当于或优于“胜安”、“三江”。"]
[null,null,"中国—东盟传统医药文化交流中心配电工程-土建工程",{"$nulls":3},59481.88]
[null,null,"分部分项工程",{"$nulls":3},57552.06]
[null,null,"A.1 土（石）方工程",{"$nulls":3},739.41]
["66","010103001001","配电房回填素土","","35.60",20.77,739.41]
[null,null,"1.填方材料品种:本工程多余土方"]
[null,null,"A.3 砌筑工程",{"$nulls":3},6039.41]
["67","010401004001","240多孔砖墙","","12.06",500.78,6039.41]
[null,null,"1.砖品种、规格、强度等级:MU10页岩烧结多孔砖；"]
[null,null,"2.砂浆种类、强度等级:M7.5水泥砂浆。"]
[null,null,"A.4 混凝土及钢筋混凝土工程",{"$nulls":3},16040.94]
["68","010501001001","C15垫层","","5.93",{"v":463.2,"d":"463.20"},2746.78]
[null,null,"1.混凝土种类:商品砼；"]
[null,null,"2.混凝土强度等级:C15。"]
["69","010502002001","构造柱","","1.04",536.59,558.05]
[null,null,"1.混凝土种类:商品砼；"]
[null,null,"2.混凝土强度等级:C25。"]
["70","010503004001","圈梁","","4.36",525.72,2292.14]
[null,null,"1.混凝土种类:商品砼；"]
[null,null,"2.混凝土强度等级:C25。"]
["71","010515001001","现浇构件圆钢筋制安 φ10以内","t","0.211",6702.61,1414.25]
["72","010515001002","现浇构件螺纹钢制安 10以上","t","0.552",6453.42,3562.29]
["73","010516002001","预埋铁件","t","0.617",8861.31,5467.43]
[null,null,"1.钢材种类:热镀锌槽钢、角钢。"]
[null,null,"A.9 楼地面工程",{"$nulls":3},32131.44]
["74","011102003001","600*600乳白色防滑砖地面","㎡","89.49",140.22,12548.29]
[null,null,"1.8-10厚地砖铺实拍平，水泥浆擦缝；"]
[null,null,"2.20厚1:4干硬性水泥砂浆；"]
[null,null,"3.素水泥浆结合层一遍。"]
[null,null,"4.面砖相当于“新中源”、“长城”"]
["75","011103001001","绝缘垫","㎡","30.00",58.38,{"v":1751.4,"d":"1751.40"}]
[null,null,"1.长度与电柜宽度相等，宽度为800~1000mm。"]
[null,null,"2.厚度：3mm厚"]
[{"$nulls":7},"表-08"]
["分部分项工程和单价措施项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":5},"第8页 共9页"]
["序\r\n\r\n号","项目编码","项目名称及\r\n项目特征描述","计量单位","工程量","金额(元)"]
[{"$nulls":5},"综合单价","合 价","其中："]
[{"$nulls":7},"暂估价"]
["76","FA060301000001","沟盖板金属盖板","t","1.660",10104.65,16773.72]
[null,null,"1.6厚花纹钢板；"]
[null,null,"2.做法详见图集02J331第95页，钢盖板仿GB6-1。"]
["77","011502007001","安全警示线","m","30.00",{"v":10,"d":"10.00"},{"v":300,"d":"300.00"}]
[null,null,"1.距离屏面一般为300~800mm，可根据实际情况进行调整。"]
["78","040205006001","黄色网格标线","㎡","20.70",36.62,758.03]
[null,null,"1.热熔网格标线。"]
[null,null,"A.10 墙、柱面工程",{"$nulls":3},2181.95]
["79","011201001001","电缆沟抹灰","㎡","92.77",23.52,2181.95]
[null,null,"1.20厚1:2.5水泥砂浆渗入水泥用量5%的防水剂。"]
[null,null,"A.13 油漆、涂料、裱糊工程",{"$nulls":3},418.91]
["80","011405001001","金属面油漆","㎡","57.86",7.24,418.91]
[null,null,"1.钢盖板刷灰漆。"]
[null,null,"单价措施项目",{"$nulls":3},1929.82]
[null,"011702","混凝土模板及支架(撑)",{"$nulls":3},1929.82]
["81","011702003001","构造柱 胶合板模板 木支撑","㎡","8.64",53.38,{"v":461.2,"d":"461.20"}]
["82","011702008001","圈梁 直形 胶合板模板 木支撑","㎡","36.37",40.38,1468.62]
[null,null,"高度按变更图 200高"]
[null,null,"中国—东盟传统医药文化交流中心配电工程-市政工程",{"$nulls":3},15034.68]
[null,null,"分部分项工程",{"$nulls":3},15034.68]
[null,null,"土石方工程",{"$nulls":3},12305.36]
["83","040101002001","挖沟槽土方 装车","","96.90",6.25,605.63]
[null,null,"1.土壤类别:三类土；"]
[null,null,"2.部位:电缆管沟。"]
["84","040103001001","沟槽回填方","","74.06",131.09,9708.53]
[null,null,"1.填方材料品种:杂砂石夯填。"]
["85","040103002001","余方弃置","","35.60",5.67,201.85]
[null,null,"1.废弃料品种:土方；"]
[null,null,"2.运距:0.5KM至配电房，用于配电房回填。"]
["86","040103002002","余方弃置","","61.30",29.19,1789.35]
[null,null,"1.废弃料品种:土方；"]
[null,null,"2.运距:10KM。"]
[null,null,"3.含加盖汽车摊销费、渣土消纳费"]
[null,null,"管网工程",{"$nulls":3},2729.32]
["87","040305001001","管沟C15垫层","","4.01",498.53,1999.11]
[{"$nulls":7},"表-08"]
["分部分项工程和单价措施项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":5},"第9页 共9页"]
["序\r\n\r\n号","项目编码","项目名称及\r\n项目特征描述","计量单位","工程量","金额(元)"]
[{"$nulls":5},"综合单价","合 价","其中："]
[{"$nulls":7},"暂估价"]
[null,null,"1.混凝土种类:商品砼；"]
[null,null,"2.混凝土强度等级:C15。"]
["88","040305001002","电缆保护管接头C20包封","","0.93",785.17,730.21]
[null,null,"1.混凝土种类:商品砼；"]
[null,null,"2.混凝土强度等级:C20。"]
[null,null,"     合    计",{"$nulls":3},1391233.27]
[null,null,"     ∑人工费",{"$nulls":3},62065.12]
[null,null,"     ∑材料费",{"$nulls":3},1281990.64]
[null,null,"     ∑机械费",{"$nulls":3},14510.02]
[null,null,"     ∑管理费",{"$nulls":3},22888.55]
[null,null,"     ∑利  润",{"$nulls":3},9778.92]
{"$rows_empty":26}
[{"$nulls":7},"表-08"]

{"sheet":"表-09_工程量清单综合单价分析表(主材)","index":5,"n_rows":470,"n_cols":13,"rows_kept":470,"merged":[[0,0,0,12],[1,0,1,8],[1,9,1,12],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,4,4,4],[2,5,4,5],[2,6,2,12],[3,6,4,6],[3,7,3,8],[3,9,4,9],[3,10,4,10],[3,11,4,11],[3,12,4,12],[28,0,28,12],[29,0,29,8],[29,9,29,12],[30,0,32,0],[30,1,32,1],[30,2,32,2],[30,3,32,3],[30,4,32,4],[30,5,32,5],[30,6,30,12],[31,6,32,6],[31,7,31,8],[31,9,32,9],[31,10,32,10],[31,11,32,11],[31,12,32,12],[56,0,56,12],[57,0,57,8],[57,9,57,12],[58,0,60,0],[58,1,60,1],[58,2,60,2],[58,3,60,3],[58,4,60,4],[58,5,60,5],[58,6,58,12],[59,6,60,6],[59,7,59,8],[59,9,60,9],[59,10,60,10],[59,11,60,11],[59,12,60,12],[85,0,85,12],[86,0,86,8],[86,9,86,12],[87,0,89,0],[87,1,89,1],[87,2,89,2],[87,3,89,3],[87,4,89,4],[87,5,89,5],[87,6,87,12],[88,6,89,6],[88,7,88,8],[88,9,89,9],[88,10,89,10],[88,11,89,11],[88,12,89,12],[113,0,113,12],[114,0,114,8],[114,9,114,12],[115,0,117,0],[115,1,117,1],[115,2,117,2],[115,3,117,3],[115,4,117,4],[115,5,117,5],[115,6,115,12],[116,6,117,6],[116,7,116,8],[116,9,117,9],[116,10,117,10],[116,11,117,11],[116,12,117,12],[141,0,141,12],[142,0,142,8],[142,9,142,12],[143,0,145,0],[143,1,145,1],[143,2,145,2],[143,3,145,3],[143,4,145,4],[143,5,145,5],[143,6,143,12],[144,6,145,6],[144,7,144,8],[144,9,145,9],[144,10,145,10],[144,11,145,11],[144,12,145,12],[164,0,164,12],[165,0,165,8],[165,9,165,12],[166,0,168,0],[166,1,168,1],[166,2,168,2],[166,3,168,3],[166,4,168,4],[166,5,168,5],[166,6,166,12],[167,6,168,6],[167,7,167,8],[167,9,168,9],[167,10,168,10],[167,11,168,11],[167,12,168,12],[189,0,189,12],[190,0,190,8],[190,9,190,12],[191,0,193,0],[191,1,193,1],[191,2,193,2],[191,3,193,3],[191,4,193,4],[191,5,193,5],[191,6,191,12],[192,6,193,6],[192,7,192,8],[192,9,193,9],[192,10,193,10],[192,11,193,11],[192,12,193,12],[217,0,217,12],[218,0,218,8],[218,9,218,12],[219,0,221,0],[219,1,221,1],[219,2,221,2],[219,3,221,3],[219,4,221,4],[219,5,221,5],[219,6,219,12],[220,6,221,6],[220,7,220,8],[220,9,221,9],[220,10,221,10],[220,11,221,11],[220,12,221,12],[245,0,245,12],[246,0,246,8],[246,9,246,12],[247,0,249,0],[247,1,249,1],[247,2,249,2],[247,3,249,3],[247,4,249,4],[247,5,249,5],[247,6,247,12],[248,6,249,6],[248,7,248,8],[248,9,249,9],[248,10,249,10],[248,11,249,11],[248,12,249,12],[273,0,273,12],[274,0,274,8],[274,9,274,12],[275,0,277,0],[275,1,277,1],[275,2,277,2],[275,3,277,3],[275,4,277,4],[275,5,277,5],[275,6,275,12],[276,6,277,6],[276,7,276,8],[276,9,277,9],[276,10,277,10],[276,11,277,11],[276,12,277,12],[300,0,300,12],[301,0,301,8],[301,9,301,12],[302,0,304,0],[302,1,304,1],[302,2,304,2],[302,3,304,3],[302,4,304,4],[302,5,304,5],[302,6,302,12],[303,6,304,6],[303,7,303,8],[303,9,304,9],[303,10,304,10],[303,11,304,11],[303,12,304,12],[326,0,326,12],[327,0,327,8],[327,9,327,12],[328,0,330,0],[328,1,330,1],[328,2,330,2],[328,3,330,3],[328,4,330,4],[328,5,330,5],[328,6,328,12],[329,6,330,6],[329,7,329,8],[329,9,330,9],[329,10,330,10],[329,11,330,11],[329,12,330,12],[355,0,355,12],[356,0,356,8],[356,9,356,12],[357,0,359,0],[357,1,359,1],[357,2,359,2],[357,3,359,3],[357,4,359,4],[357,5,359,5],[357,6,357,12],[358,6,359,6],[358,7,358,8],[358,9,359,9],[358,10,359,10],[358,11,359,11],[358,12,359,12],[384,0,384,12],[385,0,385,8],[385,9,385,12],[386,0,388,0],[386,1,388,1],[386,2,388,2],[386,3,388,3],[386,4,388,4],[386,5,388,5],[386,6,386,12],[387,6,388,6],[387,7,387,8],[387,9,388,9],[387,10,388,10],[387,11,388,11],[387,12,388,12],[412,0,412,12],[413,0,413,8],[413,9,413,12],[414,0,416,0],[414,1,416,1],[414,2,416,2],[414,3,416,3],[414,4,416,4],[414,5,416,5],[414,6,414,12],[415,6,416,6],[415,7,415,8],[415,9,416,9],[415,10,416,10],[415,11,416,11],[415,12,416,12],[441,0,441,12],[442,0,442,8],[442,9,442,12],[443,0,445,0],[443,1,445,1],[443,2,445,2],[443,3,445,3],[443,4,445,4],[443,5,445,5],[443,6,443,12],[444,6,445,6],[444,7,444,8],[444,9,445,9],[444,10,445,10],[444,11,445,11],[444,12,445,12]],"flags":["formulas_cached_only"]}
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第1页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,null,"中国—东盟传统医药文化交流中心配电工程-安装工程"]
[null,null,"分部分项工程"]
[null,null,"B4 电气设备安装工程（高低压系统）"]
["1","030401002001","干式变压器 SCB13-1000KVA","台","2",126863.17,753.86,116.22,{"v":125000,"d":"125000.00"},449.52,{"v":370.4,"d":"370.40"},173.17]
[null,null,"1.规格：SCB13-1000KVA，D,yn11 Uk=6%；"]
[null,null,"2.高压调节范围：10.5±2*2.5%/0.4KV；"]
[null,null,"3.带风机、温显温控系统、IP31外壳；"]
[null,null,"4.变压器噪音水平应低于：白昼55dB(A)、夜间45dB(A)；"]
[null,null,"5.变压器应符合入网要求、品牌相当于“ABB”或者“施奈德”"]
[null,"B4-0012换","干式变压器 SCB13-1000KVA","台","2",126863.17,753.86,116.22,{"v":125000,"d":"125000.00"},449.52,{"v":370.4,"d":"370.40"},173.17]
["2","030402017001","高压成套配电柜 进线柜AH1","台","1",77681.89,437.99,54.14,76787.26,140.98,178.21,83.31]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“南宁乔顿”"]
[null,"B4-0090换","高压成套配电柜 进线柜AH1","台","1",77681.89,437.99,54.14,76787.26,140.98,178.21,83.31]
["3","030402017002","高压成套配电柜 出线柜AH2","台","1",75615.34,437.99,54.14,74720.71,140.98,178.21,83.31]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“南宁乔顿”"]
[null,"B4-0090换","高压成套配电柜 出线柜AH2","台","1",75615.34,437.99,54.14,74720.71,140.98,178.21,83.31]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第2页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
["4","030402017003","高压成套配电柜 出线柜AH3","台","1",75615.34,437.99,54.14,74720.71,140.98,178.21,83.31]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“南宁乔顿”"]
[null,"B4-0090换","高压成套配电柜 出线柜AH3","台","1",75615.34,437.99,54.14,74720.71,140.98,178.21,83.31]
["5","030404004001","低压开关柜 进线柜1AA1","台","1",65257.34,301.63,64.26,64595.18,110.23,126.77,59.27]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0268","低压开关柜 进线柜1AA1","台","1",65257.34,301.63,64.26,64595.18,110.23,126.77,59.27]
["6","030404009001","低压电容器柜 补偿柜1AA2","台","1",61603.41,183.18,38.52,61116.24,125.87,95.13,44.47]
[null,null,"1.规格:800*1000*2200mm；380V 300kvar"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0279","低压电容器柜 补偿柜1AA2","台","1",61603.41,183.18,38.52,61116.24,125.87,95.13,44.47]
["7","030404004002","低压开关柜 出线柜1AA3","台","1",29356.63,301.63,64.26,28694.47,110.23,126.77,59.27]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第3页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0268","低压开关柜 出线柜1AA3","台","1",29356.63,301.63,64.26,28694.47,110.23,126.77,59.27]
["8","030404004003","低压开关柜 出线柜1AA4","台","1",29694.86,301.63,64.26,{"v":29032.7,"d":"29032.70"},110.23,126.77,59.27]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0268","低压开关柜 出线柜1AA4","台","1",29694.86,301.63,64.26,{"v":29032.7,"d":"29032.70"},110.23,126.77,59.27]
["9","030404004004","低压开关柜 出线柜1AA5","台","1",30098.13,301.63,64.26,29435.97,110.23,126.77,59.27]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0268","低压开关柜 出线柜1AA5","台","1",30098.13,301.63,64.26,29435.97,110.23,126.77,59.27]
["10","030404004005","低压开关柜 出线柜1AA6","台","1",31595.08,301.63,64.26,30932.92,110.23,126.77,59.27]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0268","低压开关柜 出线柜1AA6","台","1",31595.08,301.63,64.26,30932.92,110.23,126.77,59.27]
["11","030404004006","低压开关柜 进线柜2AA1","台","1",65257.34,301.63,64.26,64595.18,110.23,126.77,59.27]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第4页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,null,"3.柜体底部及孔洞防火封堵做法详见图纸；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0268","低压开关柜 进线柜2AA1","台","1",65257.34,301.63,64.26,64595.18,110.23,126.77,59.27]
["12","030404009002","低压电容器柜 补偿柜2AA2","台","1",61603.41,183.18,38.52,61116.24,125.87,95.13,44.47]
[null,null,"1.规格:800*1000*2200mm；380V 300kvar"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0279","低压电容器柜 补偿柜2AA2","台","1",61603.41,183.18,38.52,61116.24,125.87,95.13,44.47]
["13","030404004007","低压开关柜 联络柜2AA3","台","1",59775.04,301.63,64.26,59112.88,110.23,126.77,59.27]
[null,null,"1.规格:800*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0268","低压开关柜 联络柜2AA3","台","1",59775.04,301.63,64.26,59112.88,110.23,126.77,59.27]
["14","030404004008","低压开关柜 出线柜2AA4","台","1",30254.24,301.63,64.26,29592.08,110.23,126.77,59.27]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0268","低压开关柜 出线柜2AA4","台","1",30254.24,301.63,64.26,29592.08,110.23,126.77,59.27]
["15","030404004009","低压开关柜 出线柜2AA5","台","1",35590.66,301.63,64.26,{"v":34928.5,"d":"34928.50"},110.23,126.77,59.27]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第5页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0268","低压开关柜 出线柜2AA5","台","1",35590.66,301.63,64.26,{"v":34928.5,"d":"34928.50"},110.23,126.77,59.27]
["16","030404004010","低压开关柜 出线柜2AA6","台","1",31813.44,301.63,64.26,31151.28,110.23,126.77,59.27]
[null,null,"1.规格:600*1000*2200mm；"]
[null,null,"2.内部元件详见图纸系统图；"]
[null,null,"3.柜体之间连接母线、基础制作安装另计；"]
[null,null,"4.符合入网要求、元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0268","低压开关柜 出线柜2AA6","台","1",31813.44,301.63,64.26,31151.28,110.23,126.77,59.27]
["17","030414007001","在线式不间断电源 UPS-2KVA","套","1",3293.84,444.62,37.63,{"v":2400,"d":"2400.00"},145.18,181.54,84.87]
[null,"B4-0285","在线式不间断电源 UPS-2KVA","套","1",3293.84,444.62,37.63,{"v":2400,"d":"2400.00"},145.18,181.54,84.87]
["18","030403003001","带形铜母线安装 TMY-80*8mm2","m","32.20",519.64,20.46,18.86,464.07,4.83,7.78,3.64]
[null,null,"1.含母线绝缘支架、热缩管及其他配件。"]
[null,"B4-0144换","带形铜母线安装 每相一片 截面(m㎡ 以下) 800","10m/单相","3.22",{"v":4885.9,"d":"4885.90"},140.15,101.72,{"v":4514.7,"d":"4514.70"},45.48,57.14,26.71]
[null,"B4-0129换","穿墙套管、母线绝缘热缩管安装 母线绝缘热缩管 直径 (mm以内) 80","m","32.20",31.05,6.44,8.69,{"v":12.6,"d":"12.60"},0.28,2.07,0.97]
["19","030403003002","带形铜母线安装 TMY-100*10mm2","m","16.00",780.97,22.54,22.53,718.03,5.29,8.57,4.01]
[null,null,"1.含母线绝缘支架、热缩管及其他配件。"]
[null,"B4-0145换","带形铜母线安装 每相一片 截面(m㎡ 以下) 1000","10m/单相","1.6",{"v":7499.2,"d":"7499.20"},160.96,138.44,{"v":7054.3,"d":"7054.30"},50.14,64.98,30.38]
[null,"B4-0129换","穿墙套管、母线绝缘热缩管安装 母线绝缘热缩管 直径 (mm以内) 80","m","16.00",31.05,6.44,8.69,{"v":12.6,"d":"12.60"},0.28,2.07,0.97]
["20","030403003003","带形铜母线引下线 带形母线 TMY-80*8mm2","m","4.00",539.58,33.87,{"v":21.6,"d":"21.60"},464.07,3.26,11.43,5.35]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第6页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,null,"1.含母线绝缘支架、热缩管及其他配件。"]
[null,"B4-0168换","带形铜母线引下线 每相一片 截面(m㎡ 以下) 800","10m/单相","0.4",5085.19,274.32,129.05,{"v":4514.7,"d":"4514.70"},29.76,{"v":93.6,"d":"93.60"},43.76]
[null,"B4-0129换","穿墙套管、母线绝缘热缩管安装 母线绝缘热缩管 直径 (mm以内) 80","m","4.00",31.05,6.44,8.69,{"v":12.6,"d":"12.60"},0.28,2.07,0.97]
["21","030403003004","带形铜母线引下线 带形母线 TMY-100*10mm2","m","8.00",803.41,{"v":39.4,"d":"39.40"},23.22,718.03,3.42,13.18,6.16]
[null,null,"1.含母线绝缘支架、热缩管及其他配件。"]
[null,"B4-0169换","带形铜母线引下线 每相一片 截面(m㎡ 以下) 1000","10m/单相","0.8",7723.64,329.59,145.32,{"v":7054.3,"d":"7054.30"},31.38,111.11,51.94]
[null,"B4-0129换","穿墙套管、母线绝缘热缩管安装 母线绝缘热缩管 直径 (mm以内) 80","m","8.00",31.05,6.44,8.69,{"v":12.6,"d":"12.60"},0.28,2.07,0.97]
["22","030403006001","低压封闭式插接母线槽 2000A/4P","m","11.50",3290.99,41.06,15.25,{"v":3200,"d":"3200.00"},11.11,16.06,7.51]
[null,null,"1.部位：TM1到1AA1、TM2到2AA1、2AA3到1AA3；"]
[null,null,"2.含弯头、连接器、支架及其他配件，母线终端箱另计。"]
[null,null,"3.符合入网要求、品牌相当于或优于“广西派丰”。"]
[null,"B4-0231","低压封闭式插接母线槽 每相电流(A 以下) 2000","10m","1.150",32909.88,410.62,152.53,{"v":32000,"d":"32000.00"},111.08,160.58,75.07]
["23","030403007001","母线终端箱 2000A/4P","台","6",956.34,201.93,58.67,{"v":600,"d":"600.00"},3.12,63.11,29.51]
[null,null,"1.部位：TM1到1AA1、TM2到2AA1、2AA3到1AA3；"]
[null,null,"2.含变压器低压母线连接、低压柜母线连接及其他配件。"]
[null,"B4-0240","母线终端箱 2000A/4P","台","6",956.34,201.93,58.67,{"v":600,"d":"600.00"},3.12,63.11,29.51]
["24","030408001001","铜芯电力电缆 ZR-YJV22-8.7/15KV-3*120mm2","m","280.00",364.73,9.79,0.57,348.45,1.03,3.33,1.56]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第7页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
[null,"B4-0996换","铜芯电力电缆敷设 普通敷设 电缆(截面m㎡以下)120","100m","2.8000",36472.79,979.29,56.92,{"v":34845,"d":"34845.00"},{"v":102.8,"d":"102.80"},333.07,155.71]
["25","030408001002","铜芯电力电缆 ZR-YJV22-8.7/15KV-3*70mm2","m","38.70",{"v":232.2,"d":"232.20"},5.85,0.51,{"v":222.2,"d":"222.20"},0.69,2.01,0.94]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
[null,"B4-0995换","铜芯电力电缆敷设 普通敷设 电缆(截面m㎡以下)70","100m","0.3870",23220.51,584.91,51.33,{"v":22220,"d":"22220.00"},68.93,201.25,94.09]
["26","030408001003","铜芯电力电缆 ZR-VV-0.6/1KV-120mm2","m","10.00",84.88,6.56,0.38,73.98,0.69,2.23,1.04]
[null,null,"1.用于变压器连接低压柜PE接用；"]
[null,null,"2.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
[null,"B4-0996换","铜芯电力电缆敷设 普通敷设 电缆(截面m㎡以下)120","100m","0.1000",8489.11,656.13,38.17,7398.25,69.01,{"v":223.2,"d":"223.20"},104.35]
["27","030408006001","户内10KV冷缩电力电缆头制作、安装 70mm2","个","4",644.19,61.31,83.36,{"v":469.2,"d":"469.20"},1.81,19.43,9.08]
[null,"B4-1080换","户内冷缩式电力电缆终端头制作、安装10kV以下端头(截面m㎡以下)70","个","4",644.19,61.31,83.36,{"v":469.2,"d":"469.20"},1.81,19.43,9.08]
["28","030408006002","户内10KV冷缩电力电缆头制作、安装 120mm2","个","2",886.32,76.65,109.42,{"v":663,"d":"663.00"},1.81,24.15,11.29]
[null,"B4-1081换","户内冷缩式电力电缆终端头制作、安装10kV以下端头(截面m㎡以下)120","个","2",886.32,76.65,109.42,{"v":663,"d":"663.00"},1.81,24.15,11.29]
["29","桂030404039001","焊、压铜接线端子 120mm2","个","4",27.15,4.35,20.83,null,null,1.34,0.63]
[null,"B4-0386","焊铜接线端子 导线截面(m㎡ 以内) 120","10个","0.4",271.41,43.48,208.29,null,null,13.38,6.26]
["30","030408003001","电缆保护管 C-PVC-167*8.5","m","144.40",73.66,5.91,{"v":1.3,"d":"1.30"},61.48,1.58,2.31,1.08]
[null,null,"1.含管枕、配件，管沟土方挖填另计。"]
[null,null,"2.品牌相当于或优于“雄塑”、“联塑”。"]
[null,"B4-0817换","塑料管埋地敷设 C-PVC-167*8.5","100m","1.4440",7365.06,591.28,129.51,{"v":6148,"d":"6148.00"},157.88,230.59,{"v":107.8,"d":"107.80"}]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第8页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
["31","030411003001","电缆桥架 200*150*2.0mm","m","60.00",115.94,18.43,2.31,85.43,0.99,5.98,{"v":2.8,"d":"2.80"}]
[null,null,"1.含盖板、弯头、三通、配件、接地线，支架及刷油另计。"]
[null,null,"2.品牌相当于或优于“南宁乔顿”、“北乔”。"]
[null,"B4-0905换","钢制桥架 钢制槽式桥架(宽+高mm以下) 400","10m","6.000",1159.34,184.34,23.09,854.25,9.92,59.79,27.95]
["32","030408008001","高低压配电柜内壁防火堵洞","处","44",93.03,46.38,{"v":20.7,"d":"20.70"},{"v":5,"d":"5.00"},null,14.28,6.67]
[null,null,"按设计说明施工"]
[null,"B4-0960","防火涂料、堵洞、 防火堵洞 盘柜下","处","44",93.03,46.38,{"v":20.7,"d":"20.70"},{"v":5,"d":"5.00"},null,14.28,6.67]
["33","030408009001","高低压配电柜内壁防火隔板","㎡","11.08",209.18,81.16,36.36,{"v":55,"d":"55.00"},null,24.98,11.68]
[null,null,"按设计说明施工"]
[null,"B4-0963换","防火涂料、堵洞、 防火隔板","㎡","11.08",209.18,81.16,36.36,{"v":55,"d":"55.00"},null,24.98,11.68]
["34","030408010001","高低压配电柜内壁防火涂料","kg","8.20",24.63,15.07,0.55,{"v":2.2,"d":"2.20"},null,4.64,2.17]
[null,null,"按设计说明施工"]
[null,"B4-0964","防火涂料、堵洞、防火涂料","10kg","0.820",246.31,150.72,5.51,{"v":22,"d":"22.00"},null,46.39,21.69]
["35","030408008002","电缆桥架穿墙体防火封堵","处","5",435.25,139.13,18.28,{"v":215,"d":"215.00"},null,42.82,20.02]
[null,null,"1.做法详见图纸。"]
[null,"B4-0961","防火涂料、堵洞、隔板及阻燃槽盒 防火堵洞 电缆隧道","处","5",435.25,139.13,18.28,{"v":215,"d":"215.00"},null,42.82,20.02]
["36","030413001001","桥架支架制作、安装","kg","108.99",17.72,4.99,3.73,5.87,0.61,1.72,{"v":0.8,"d":"0.80"}]
[null,null,"1.支架采用角钢，除锈、刷油另计。"]
[null,null,"2.按设计图纸施工(HX-P19035ZBS-AO 1-35)。"]
[null,"B4-2001换","一般铁构件制作安装","100kg","1.0899",1772.21,498.53,373.05,587.24,60.76,172.15,80.48]
["37","030413001002","电缆支架","kg","223.94",18.78,4.99,3.73,6.93,0.61,1.72,{"v":0.8,"d":"0.80"}]
[null,null,"1.L50*5热镀锌角钢加工，每@800mm预埋一组支架，一组3层。"]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第9页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,"B4-2001换","一般铁构件制作安装","100kg","2.2394",1878.21,498.53,373.05,693.24,60.76,172.15,80.48]
["38","031201003001","金属结构刷油","kg","108.99",2.61,1.06,0.09,0.42,0.52,0.36,0.16]
[null,null,"1.手工除锈，刷防锈漆、调和漆各两道。"]
[null,"B11-0007","手工除锈 一般钢结构 轻锈","100kg","1.0899",50.67,26.09,2.15,null,10.48,8.34,3.61]
[null,"B11-0117换","金属结构刷油 一般钢结构 红丹防锈漆 第一遍","100kg","1.0899",{"v":55.8,"d":"55.80"},19.84,2.74,12.83,10.48,6.91,{"v":3,"d":"3.00"}]
[null,"B11-0118换","金属结构刷油 一般钢结构 红丹防锈漆 第二遍","100kg","1.0899",53.12,19.84,2.38,10.51,10.48,6.91,{"v":3,"d":"3.00"}]
[null,"B11-0126换","金属结构刷油 一般钢结构 调和漆 第一遍","100kg","1.0899",51.61,20.49,0.82,{"v":9.7,"d":"9.70"},10.48,7.06,3.06]
[null,"B11-0127换","金属结构刷油 一般钢结构 调和漆 第二遍","100kg","1.0899",49.44,19.84,0.73,8.48,10.48,6.91,{"v":3,"d":"3.00"}]
["39","030414001001","电力变压器系统调试 10KV以下(容量2000KV.A以下)","系统","2",7538.37,3848.33,{"v":35,"d":"35.00"},null,1320.35,1590.92,743.77]
[null,"B4-2071","电力变压器系统调试 10KV以下变压器（容量2000KV.A以下）","系统","2",7538.37,3848.33,{"v":35,"d":"35.00"},null,1320.35,1590.92,743.77]
["40","030414002001","送配电装置系统调试 1KV以下交流供电","系统","9",{"v":1206.9,"d":"1206.90"},{"v":745.8,"d":"745.80"},4.07,null,82.77,255.03,119.23]
[null,"B4-2080","送配电装置系统调试 1KV以下交流供电（综合）","系统","9",{"v":1206.9,"d":"1206.90"},{"v":745.8,"d":"745.80"},4.07,null,82.77,255.03,119.23]
["41","030414002002","送配电装置系统调试 10KV以下交流供电","系统","2",1952.74,{"v":1118.7,"d":"1118.70"},10.17,null,219.43,411.88,192.56]
[null,"B4-2081","送配电装置系统调试 10KV以下交流供电  负荷隔离开关","系统","2",1952.74,{"v":1118.7,"d":"1118.70"},10.17,null,219.43,411.88,192.56]
["42","030414004001","自动投入装置调试  备用电源自投装置","系统","1",1432.62,626.47,{"v":5.7,"d":"5.70"},null,356.46,302.55,141.44]
[null,"B4-2094","自动投入装置调试  备用电源自投装置","系统","1",1432.62,626.47,{"v":5.7,"d":"5.70"},null,356.46,302.55,141.44]
["43","030414008001","母线调试 母线系统 1KV以下","段","3",535.88,268.49,2.45,null,98.96,{"v":113.1,"d":"113.10"},52.88]
[null,"B4-2115","母线、避雷器、电容器调试  母线系统 1 KV以下","段","3",535.88,268.49,2.45,null,98.96,{"v":113.1,"d":"113.10"},52.88]
["44","030414008002","母线调试 母线系统 10KV以下","段","1",1977.72,984.46,8.96,null,371.72,417.43,195.15]
[null,"B4-2116","母线、避雷器、电容器调试  母线系统 10 KV以下","段","1",1977.72,984.46,8.96,null,371.72,417.43,195.15]
["45","030414009001","避雷器调试 1KV以下","组","4",560.07,277.81,3.22,null,105.77,118.07,{"v":55.2,"d":"55.20"}]
[null,"B4-2117","母线、避雷器、电容器调试  避雷器 1 KV以下","组","4",560.07,277.81,3.22,null,105.77,118.07,{"v":55.2,"d":"55.20"}]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第10页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
["46","030414009002","避雷器调试 10KV以下","组","1",1017.31,536.98,4.88,null,160.43,214.66,100.36]
[null,"B4-2118","母线、避雷器、电容器调试  避雷器 10 KV以下","组","1",1017.31,536.98,4.88,null,160.43,214.66,100.36]
["47","030414010001","电容器调试 1KV以下","组","2",456.53,223.74,2.03,null,89.34,96.37,45.05]
[null,"B4-2119","母线、避雷器、电容器调试  电容器 1 KV以下","组","2",456.53,223.74,2.03,null,89.34,96.37,45.05]
["48","030414015001","电缆试验 泄露试验","根","3",186.75,98.45,0.53,null,29.83,39.48,18.46]
[null,"B4-2144","绝缘子、套管、绝缘油、电缆试验  电缆试验  泄露试验","根次","3",186.75,98.45,0.53,null,29.83,39.48,18.46]
["49","030414015002","电缆试验 交流耐压试验","根","3",590.99,318.83,1.57,null,87.19,124.97,58.43]
[null,"B4-2145","绝缘子、套管、绝缘油、电缆试验  电缆试验  交流耐压试验","１０KV组/三相","3",590.99,318.83,1.57,null,87.19,124.97,58.43]
[null,null,"B4 电气设备安装工程（配电房照明）"]
["50","030404017001","室内照明配电箱","台","1",{"v":625.4,"d":"625.40"},86.95,24.51,{"v":460,"d":"460.00"},{"v":10.1,"d":"10.10"},29.87,13.97]
[null,null,"1.304不锈钢材质；"]
[null,null,"2.安装方式:底边距地1.3米暗装；"]
[null,null,"3.内部元件详见图纸系统图；"]
[null,null,"4.箱内元件品牌相当于或优于“ABB”、“施耐德”。"]
[null,"B4-0301换","成套配电箱安装 悬挂嵌入式(半周长m) 0.5","台","1",{"v":625.4,"d":"625.40"},86.95,24.51,{"v":460,"d":"460.00"},{"v":10.1,"d":"10.10"},29.87,13.97]
["51","030404034001","双极双控开关 20A 220V","套","2",{"v":26,"d":"26.00"},9.13,1.73,11.02,null,2.81,1.31]
[null,null,"1.安装方式:底边距地1.3米暗装。"]
[null,null,"2.品牌相当于或优于“TCL”、“西蒙”。"]
[null,"B4-0419换","开关、按钮、插座安装 开关及按钮 跷板暗开关(双控) 双联","10套","0.2",260.03,91.34,17.28,110.16,null,28.11,13.14]
["52","030404035001","两孔三孔暗插座 16A 220V","套","8",27.43,10.33,2.41,10.02,null,3.18,1.49]
[null,null,"1.安装方式:底边距地0.3米暗装。"]
[null,null,"2.品牌相当于或优于“TCL”、“西蒙”。"]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第11页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,"B4-0436换","单、三相暗插座 单相暗插座10A 5孔","10套","0.8",274.24,103.32,24.09,100.16,null,{"v":31.8,"d":"31.80"},14.87]
["53","030412005001","双管普通日光灯 2*24W","套","18",82.29,18.43,2.29,53.01,0.16,5.72,2.68]
[null,null,"1.安装方式:吸顶安装。"]
[null,null,"2.品牌相当于或优于“三雄极光”、“欧普”。"]
[null,"B4-1886换","荧光灯具安装 壁装式、吸顶式  双管","10套","1.8",822.82,184.34,{"v":22.9,"d":"22.90"},530.05,1.56,57.22,26.75]
["54","030412004001","安全出口标志","套","1",91.69,15.88,2.75,65.65,0.16,4.94,2.31]
[null,null,"1.安装方式:门框上方0.2米壁装。"]
[null,null,"2.品牌相当于或优于“广威消防”、“安尔顿照明”。"]
[null,"B4-1846换","装饰灯具安装 标志、诱导装饰灯、应急灯 墙壁式","10套","0.1",916.73,158.78,27.47,{"v":656.5,"d":"656.50"},1.56,49.35,23.07]
["55","030412004002","单向疏散灯","套","6",101.79,15.88,2.75,75.75,0.16,4.94,2.31]
[null,null,"1.安装方式:距地0.3米壁装。"]
[null,null,"2.品牌相当于或优于“广威消防”、“安尔顿照明”。"]
[null,"B4-1846换","装饰灯具安装 标志、诱导装饰灯、应急灯 墙壁式","10套","0.6",1017.73,158.78,27.47,{"v":757.5,"d":"757.50"},1.56,49.35,23.07]
["56","030108003001","轴流风机 160W","台","4",1074.92,202.33,110.25,{"v":655.3,"d":"655.30"},10.78,65.59,30.67]
[null,null,"1.含2个进风防火阀，2个排风防火阀及配电房门防鼠网；"]
[null,null,"2.安装方式:距地3.5米壁装。"]
[null,null,"3.品牌相当于或优于“美的”、“金羚”。"]
[null,"B7-0055","轴流风机 160W","台","4",682.92,106.28,74.53,{"v":450,"d":"450.00"},2.83,33.58,{"v":15.7,"d":"15.70"}]
[null,"B7-0319换","风管防火阀安装 2200mm周长以内","个","4",244.66,45.73,25.28,{"v":150,"d":"150.00"},2.06,14.71,6.88]
[null,"B4-2004换","网门、保护网制作、安装","㎡","1.60",368.36,125.79,26.11,138.26,14.73,43.25,20.22]
["57","030408001004","铜芯电力电缆 WDZN-YJV-0.6/1KV-4*25mm2","m","50.00",{"v":105.2,"d":"105.20"},3.64,0.46,99.05,0.28,1.21,0.56]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第12页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
[null,"B4-0994换","铜芯电力电缆敷设 普通敷设 电缆(截面m㎡以下)35","100m","0.5000",10519.32,363.92,45.85,9905.07,27.62,120.52,56.34]
["58","030411004001","管内穿线 照明线路 NH-BV-0.4/1KV-2.5mm2","m","600.00",{"v":3.3,"d":"3.30"},{"v":0.5,"d":"0.50"},{"v":0.2,"d":"0.20"},2.38,null,0.15,0.07]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
[null,"B4-1564换","管内穿线 照明线路 铜芯 导线截面(m㎡以内) 2.5","100m单线","6",330.78,50.24,20.25,{"v":237.6,"d":"237.60"},null,15.46,7.23]
["59","030411004002","管内穿线 动力线路 NH-BV-0.4/1KV-4mm2","m","300.00",4.44,0.53,{"v":0.2,"d":"0.20"},3.47,null,0.16,0.08]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
[null,"B4-1583换","管内穿线 动力线路 铜芯 导线截面(m㎡以内) 4","100m单线","3",444.28,53.46,20.18,{"v":346.5,"d":"346.50"},null,16.45,7.69]
["60","030411004003","管内穿线 动力线路 NH-BV-0.4/1KV-6mm2","m","300.00",6.22,0.57,0.21,5.18,null,0.18,0.08]
[null,null,"1.电缆品牌相当于或优于“广西网联”、“昆明明超”。"]
[null,"B4-1584换","管内穿线 动力线路 铜芯 导线截面(m㎡以内) 6","100m单线","3",621.25,57.07,20.75,517.65,null,17.57,8.21]
["61","030411001001","砖、混凝土结构暗配 KBG可挠金属管 φ16","m","400.00",10.68,4.85,1.78,1.86,null,1.49,{"v":0.7,"d":"0.70"}]
[null,null,"品牌相当于或优于“雄塑”、“联塑”。"]
[null,"B4-1520换","砖、混凝土结构暗配 扣压式(KBG)、紧定式(JDG)电气钢导管规格 16","100m","4.0000",1068.38,484.62,178.42,186.43,null,149.17,69.74]
["62","030409001001","接地极 L50*5热镀锌角钢 L=2.5M","根","12",{"v":115.9,"d":"115.90"},27.82,1.34,59.75,9.94,11.62,5.43]
[null,null,"1.部位：室外管沟内。"]
[null,"B4-1188换","接地极(板)制作、安装 角钢接地极 普通土","根","12",{"v":115.9,"d":"115.90"},27.82,1.34,59.75,9.94,11.62,5.43]
["63","030409002001","户内接地母线 -50*5热镀锌扁钢","m","92.06",26.36,7.94,{"v":0.7,"d":"0.70"},13.25,0.61,2.63,1.23]
[null,null,"1.部位：配电房内。"]
[null,"B4-1200换","钢接地母线敷设 户内钢接地母线敷设","10m","9.206",263.66,79.42,7.03,132.51,6.08,26.32,{"v":12.3,"d":"12.30"}]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第13页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
["64","030414011001","接地装置调试  独立接地装置","系统","1",335.13,178.99,1.63,null,50.74,70.71,33.06]
[null,"B4-2122","接地装置调试  独立接地装置","组","1",335.13,178.99,1.63,null,50.74,70.71,33.06]
[null,null,"B9 给排水、燃气工程"]
["65","030901013001","灭火器及箱体","套","3",218.87,12.68,0.46,{"v":200,"d":"200.00"},null,{"v":3.9,"d":"3.90"},1.83]
[null,null,"1.箱体规格:600*100*800mm；"]
[null,null,"2.内含两具灭火器。"]
[null,null,"3.品牌相当于或优于“胜安”、“三江”。"]
[null,"B9-0854换","灭火器放置箱安装 放置式 箱半周长 1m 以内","10个","0.3",2188.73,126.82,4.62,{"v":2000,"d":"2000.00"},null,39.04,18.25]
[null,null,"中国—东盟传统医药文化交流中心配电工程-土建工程"]
[null,null,"分部分项工程"]
[null,null,"A.1 土（石）方工程"]
["66","010103001001","配电房回填素土","","35.60",20.77,16.29,null,null,2.27,1.76,0.45]
[null,null,"1.填方材料品种:本工程多余土方"]
[null,"A1-82","人工回填土 夯填","100","0.3560",2077.43,1628.64,null,null,227.04,176.29,45.46]
[null,null,"A.3 砌筑工程"]
["67","010401004001","240多孔砖墙","","12.06",500.78,129.75,312.26,null,3.36,44.15,11.26]
[null,null,"1.砖品种、规格、强度等级:MU10页岩烧结多孔砖；"]
[null,null,"2.砂浆种类、强度等级:M7.5水泥砂浆。"]
[null,"A3-11换","混水砖墙 多孔砖240×115×90 墙体厚度 24cm{换:水泥砂浆中砂M7.5}","10","1.206",5007.86,1297.49,3122.58,null,33.64,441.54,112.61]
[null,null,"A.4 混凝土及钢筋混凝土工程"]
["68","010501001001","C15垫层","","5.93",{"v":463.2,"d":"463.20"},58.55,{"v":379.2,"d":"379.20"},null,0.76,19.67,5.02]
[null,null,"1.混凝土种类:商品砼；"]
[null,null,"2.混凝土强度等级:C15。"]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第14页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,"A4-3换","混凝土垫层{换:碎石 GD40  商品普通砼  C15}","10","0.593",{"v":4631.9,"d":"4631.90"},585.47,3791.98,null,7.57,196.71,50.17]
["69","010502002001","构造柱","","1.04",536.59,{"v":94.7,"d":"94.70"},400.68,null,1.26,31.83,8.12]
[null,null,"1.混凝土种类:商品砼；"]
[null,null,"2.混凝土强度等级:C25。"]
[null,"A4-20换","混凝土柱 构造柱{换:碎石 GD40  商品普通砼  C25}","10","0.104",5365.81,946.96,{"v":4006.8,"d":"4006.80"},null,12.59,318.28,81.18]
["70","010503004001","圈梁","","4.36",525.72,85.29,403.82,null,0.78,28.55,7.28]
[null,null,"1.混凝土种类:商品砼；"]
[null,null,"2.混凝土强度等级:C25。"]
[null,"A4-24换","混凝土 圈梁{换:碎石 GD40  商品普通砼  C25}","10","0.436",5257.17,852.85,4038.21,null,7.82,285.48,72.81]
["71","010515001001","现浇构件圆钢筋制安 φ10以内","t","0.211",6702.61,709.14,5679.17,null,13.48,239.69,61.13]
[null,"A4-236","现浇构件圆钢筋制安 φ10以内","t","0.211",6702.61,709.14,5679.17,null,13.48,239.69,61.13]
["72","010515001002","现浇构件螺纹钢制安 10以上","t","0.552",6453.42,520.92,5574.57,null,{"v":99.6,"d":"99.60"},205.83,{"v":52.5,"d":"52.50"}]
[null,"A4-241","现浇构件螺纹钢制安 10以上","t","0.552",6453.42,520.92,5574.57,null,{"v":99.6,"d":"99.60"},205.83,{"v":52.5,"d":"52.50"}]
["73","010516002001","预埋铁件","t","0.617",8861.31,1963.65,{"v":6080.2,"d":"6080.20"},null,null,651.34,166.12]
[null,null,"1.钢材种类:热镀锌槽钢、角钢。"]
[null,"A4-326","铁件 预埋铁件","t","0.617",8861.31,1963.65,{"v":6080.2,"d":"6080.20"},null,null,651.34,166.12]
[null,null,"A.9 楼地面工程"]
["74","011102003001","600*600乳白色防滑砖地面","㎡","89.49",140.22,26.34,{"v":101.9,"d":"101.90"},null,2.18,7.79,2.01]
[null,null,"1.8-10厚地砖铺实拍平，水泥浆擦缝；"]
[null,null,"2.20厚1:4干硬性水泥砂浆；"]
[null,null,"3.素水泥浆结合层一遍。"]
[null,null,"4.面砖相当于“新中源”、“长城”"]
[null,"A9-83换","陶瓷地砖楼地面 每块周长(2400mm以内)  水泥砂浆 密缝{素水泥浆}","100㎡","0.8949",14021.47,2634.06,10189.96,null,217.61,778.51,201.33]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第15页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
["75","011103001001","绝缘垫","㎡","30.00",58.38,7.76,47.95,null,null,2.12,0.55]
[null,null,"1.长度与电柜宽度相等，宽度为800~1000mm。"]
[null,null,"2.厚度：3mm厚"]
[null,"A9-115换","楼地面 橡胶板","100㎡","0.3000",5838.31,776.49,4795.02,null,null,211.98,54.82]
["76","FA060301000001","沟盖板金属盖板","t","1.660",10104.65,{"v":1753.2,"d":"1753.20"},6288.34,null,941.37,893.78,227.96]
[null,null,"1.6厚花纹钢板；"]
[null,null,"2.做法详见图集02J331第95页，钢盖板仿GB6-1。"]
[null,"A6-53换","钢盖板制作","t","1.660",8379.71,{"v":847.7,"d":"847.70"},6288.34,null,628.95,{"v":489.8,"d":"489.80"},124.92]
[null,"A6-99","钢盖板 安装","t","1.660",1724.94,{"v":905.5,"d":"905.50"},null,null,312.42,403.98,103.04]
["77","011502007001","安全警示线","m","30.00",{"v":10,"d":"10.00"},null,null,{"v":10,"d":"10.00"}]
[null,null,"1.距离屏面一般为300~800mm，可根据实际情况进行调整。"]
[null,"B-","安全警示带","m","30",{"v":10,"d":"10.00"},null,null,{"v":10,"d":"10.00"}]
["78","040205006001","黄色网格标线","㎡","20.70",36.62,6.36,{"v":21.8,"d":"21.80"},null,4.67,3.01,0.78]
[null,null,"1.热熔网格标线。"]
[null,"C2-0223","热熔涂料标线","10㎡","2.070",366.18,63.61,218.02,null,46.66,{"v":30.1,"d":"30.10"},7.79]
[null,null,"A.10 墙、柱面工程"]
["79","011201001001","电缆沟抹灰","㎡","92.77",23.52,{"v":8.2,"d":"8.20"},11.39,null,0.37,2.84,0.72]
[null,null,"1.20厚1:2.5水泥砂浆渗入水泥用量5%的防水剂。"]
[null,"A7-177","防水砂浆防水 20mm厚 立面{水泥防水砂浆(加防水粉5％) 1∶2}","100㎡","0.9277",2351.98,819.55,1139.01,null,36.89,284.08,72.45]
[null,null,"A.13 油漆、涂料、裱糊工程"]
["80","011405001001","金属面油漆","㎡","57.86",7.24,3.99,1.88,null,null,1.09,0.28]
[null,null,"1.钢盖板刷灰漆。"]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第16页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,"A13-150","调和漆 金属面 二遍","100㎡","0.5786",723.89,398.97,187.83,null,null,108.92,28.17]
[null,null,"单价措施项目"]
[null,"011702","混凝土模板及支架(撑)"]
["81","011702003001","构造柱 胶合板模板 木支撑","㎡","8.64",53.38,{"v":27.5,"d":"27.50"},14.09,null,0.24,{"v":9.2,"d":"9.20"},2.35]
[null,"A17-58","构造柱 胶合板模板 木支撑","100㎡","0.0864",5338.25,2749.85,1409.21,null,24.31,920.19,234.69]
["82","011702008001","圈梁 直形 胶合板模板 木支撑","㎡","36.37",40.38,22.05,8.77,null,0.27,{"v":7.4,"d":"7.40"},1.89]
[null,null,"高度按变更图 200高"]
[null,"A17-72","圈梁 直形 胶合板模板 木支撑","100㎡","0.3637",4037.82,2205.22,876.65,null,26.77,740.35,188.83]
[null,null,"中国—东盟传统医药文化交流中心配电工程-市政工程"]
[null,null,"分部分项工程"]
[null,null,"土石方工程"]
["83","040101002001","挖沟槽土方 装车","","96.90",6.25,0.32,null,null,5.29,0.41,0.23]
[null,null,"1.土壤类别:三类土；"]
[null,null,"2.部位:电缆管沟。"]
[null,"C1-0025","挖掘机挖沟槽、基坑土方（斗容量0.4）装车 三类土","1000","0.08690",6958.93,357.12,null,null,5896.97,452.17,252.67]
["84","040103001001","沟槽回填方","","74.06",131.09,8.93,118.84,null,2.08,{"v":0.8,"d":"0.80"},0.44]
[null,null,"1.填方材料品种:杂砂石夯填。"]
[null,"C1-0100","沟槽回填机械碾压 振动压路机1t 沟槽回填（槽底宽≤2.8m）砂砾石","100","0.7406",{"v":13108.4,"d":"13108.40"},{"v":892.8,"d":"892.80"},11883.82,null,207.75,79.57,44.46]
["85","040103002001","余方弃置","","35.60",5.67,{"$nulls":3},5.09,0.37,0.21]
[null,null,"1.废弃料品种:土方；"]
[null,null,"2.运距:0.5KM至配电房，用于配电房回填。"]
[null,"C1-0120","自卸汽车运土方（运距0.5km内） 4.5t","1000","0.03560",5666.16,{"$nulls":3},5092.26,368.17,205.73]
["86","040103002002","余方弃置","","61.30",29.19,null,0.04,{"v":8,"d":"8.00"},19.01,1.37,0.77]
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]
["工程量清单综合单价分析表"]
["工程名称：中国—东盟传统医药文化交流中心配电工程",{"$nulls":8},"第17页 共17页"]
["序号","项目编码","项目名称及项目\r\n特征描述","单位","工程量","综合单价\r\n(元)","综合单价"]
[{"$nulls":6},"人工费","材料费",null,"机械费","管理费","利润","其中:\r\n暂估价"]
[{"$nulls":7},"附材费","主材费"]
[null,null,"1.废弃料品种:土方；"]
[null,null,"2.运距:10KM。"]
[null,null,"3.含加盖汽车摊销费、渣土消纳费"]
[null,"C1-0124换","自卸汽车运土方（运距1km内） 12t[实际10]","1000","0.06130",21199.24,null,{"v":42.5,"d":"42.50"},null,19013.88,{"v":1374.7,"d":"1374.70"},768.16]
[null,"B-","渣土消纳费","","61.3",{"v":8,"d":"8.00"},null,null,{"v":8,"d":"8.00"}]
[null,null,"管网工程"]
["87","040305001001","管沟C15垫层","","4.01",498.53,65.67,{"v":404.4,"d":"404.40"},null,2.91,17.79,7.76]
[null,null,"1.混凝土种类:商品砼；"]
[null,null,"2.混凝土强度等级:C15。"]
[null,"C5-2226","混凝土基础垫层 复合木模","10㎡","0.722",432.39,229.71,98.63,null,13.47,63.08,{"v":27.5,"d":"27.50"}]
[null,"C5-0720换","非定型管道垫层 混凝土{换:碎石 GD40  商品普通砼  C15}","10","0.401",4206.78,243.14,3866.39,null,4.87,64.33,28.05]
["88","040305001002","电缆保护管接头C20包封","","0.93",785.17,219.34,472.95,null,8.14,59.01,25.73]
[null,null,"1.混凝土种类:商品砼；"]
[null,null,"2.混凝土强度等级:C20。"]
[null,"C5-2222换","管道支墩(挡墩) 每处(1内){换:碎石 GD40  商品普通砼  C20}","10","0.093",{"v":4580.8,"d":"4580.80"},434.68,3977.52,null,4.87,114.02,49.71]
[null,"C5-2228","现浇混凝土模板 管道基础(平基、管座) 复合木模","10㎡","0.634",479.79,257.98,110.31,null,11.22,69.83,30.45]
{"$rows_empty":7}
[" ",null,null," ",null,null," ",null,null," "," ",null,"表－09"]

{"sheet":"表-11_总价措施项目清单与计价表","index":6,"n_rows":36,"n_cols":7,"rows_kept":36,"merged":[[0,0,0,6],[1,0,1,4],[4,3,6,3],[9,3,12,3],[15,3,18,3],[34,0,34,6]],"flags":["formulas_cached_only"]}
["总价措施项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程   ",{"$nulls":5},"第1页 共1页"]
["序\r\n号","项目编码","项 目 名 称","计 算 基 础","费 率(%)\r\n或标准","金 额(元)","备注"]
[null,null,"中国—东盟传统医药文化交流中心配电工程-安装工程",null,null,22026.36]
["1","桂031401001001","安全文明施工费","∑分部分项及单价措施费定额(人工费+机械费)",null,7153.22]
["2","桂031401002001","检验试验配合费",null,null,301]
["3","桂031401003001","雨季施工增加费",null,null,2413.92]
["4","桂031401004001","暗室施工增加费","地下室建筑面积(无规定的按暗室施工人工费×25%)",null,12158.22]
[null,null,"中国—东盟传统医药文化交流中心配电工程-土建工程",null,null,6653.59]
["1","桂011801001001","安全文明施工费","∑(分部分项人材机+单价措施人材机)\r\n(52443.32+1492.15)","7.36",3969.65]
["2","桂011801002001","检验试验配合费",null,"0.11",59.33]
["3","桂011801003001","雨季施工增加费",null,"0.53",285.86]
["4","桂011801004001","工程定位复测费",null,"0.05",26.97]
["5","桂011801005001","暗室施工增加费","暗室施工人工费","25.00",2311.78]
[null,null,"中国—东盟传统医药文化交流中心配电工程-市政工程",null,null,501.16]
["1","桂041201001001","安全文明施工费","∑分部分项、单价措施(人工费+机械费)",null,379.86]
["2","桂041201002001","检验试验配合费",null,null,15.96]
["3","桂041201003001","雨季施工增加费",null,null,95.76]
["4","桂041201004001","工程定位复测费",null,null,9.58]
[null,null,"       合     计",null,null,29181.11]
{"$rows_empty":14}
["注：以项计算的总价措施，无“计算基础”和“费率”的数值，可只填“金额”数值，但应在备注栏说明施工方案出处或计算方式。"]
[{"$nulls":6},"表-11"]

{"sheet":"表-14_税前项目清单与计价表","index":7,"n_rows":91,"n_cols":7,"rows_kept":91,"merged":[[0,0,0,6],[1,0,1,4],[1,5,1,6],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,4,4,4],[2,5,2,6],[3,5,4,5],[3,6,4,6],[43,0,43,6],[44,0,44,4],[45,0,45,6],[46,0,46,4],[46,5,46,6],[47,0,49,0],[47,1,49,1],[47,2,49,2],[47,3,49,3],[47,4,49,4],[47,5,47,6],[48,5,49,5],[48,6,49,6],[89,0,89,6],[90,0,90,4]],"flags":["formulas_cached_only"]}
["税前项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":4},"第1页 共2页"]
["序号","项目编码","项目名称及项目特征\r\n描述","计量单位","工程量","金  额(元)"]
[{"$nulls":5},"单价","合 价"]
[]
[null,null,"中国—东盟传统医药文化交流中心配电工程-土建工程",{"$nulls":3},{"v":2529,"d":"2529.00"}]
["1","011507001001","高低压配电房门牌","个","1",{"v":50,"d":"50.00"},{"v":50,"d":"50.00"}]
[null,null,"1.安装下限离地面1.6米。"]
["2","011507001002","“门口严禁停放车辆、堆放杂物”标示牌","个","1",{"v":60,"d":"60.00"},{"v":60,"d":"60.00"}]
[null,null,"1.安装下限离地面1.6米。"]
[null,null,"2.240*300 反光铝板丝印（户外漆）"]
["3","011507001003","“未经许可不得入内”标示牌","个","1",{"v":60,"d":"60.00"},{"v":60,"d":"60.00"}]
[null,null,"1.安装下限离地面1.6米。"]
[null,null,"2.240*300 反光铝板丝印（户外漆）"]
["4","011507001004","“止步高压危险”标示牌","个","4",{"v":60,"d":"60.00"},{"v":240,"d":"240.00"}]
[null,null,"1.安装下限离地面1.6米。"]
[null,null,"2.240*300 反光铝板丝印（户外漆）"]
["5","011507001005","“紧急出口”标示牌","个","1",{"v":30,"d":"30.00"},{"v":30,"d":"30.00"}]
[null,null,"1.疏散方向指示箭头指向门口，安装下限离地面0.3米。"]
["6","桂030413018001","防鼠挡板","m","3.30",{"v":230,"d":"230.00"},{"v":759,"d":"759.00"}]
[null,null,"1.高0.6米，其上部设置防止绊脚跤标示。"]
[null,null,"2.材质:铝合金"]
["7","011507001006","“灭火器箱”标示牌","个","3",{"v":30,"d":"30.00"},{"v":90,"d":"90.00"}]
[null,null,"1.安装下限比灭火设备高0.1米。"]
["8","011502007002","禁止阻塞线","个","3",{"v":150,"d":"150.00"},{"v":450,"d":"450.00"}]
[null,null,"1.禁止阻塞线范围宽度与消防设备宽度相等。"]
["9","011507001007","电房运行管理制度牌","个","1",{"v":200,"d":"200.00"},{"v":200,"d":"200.00"}]
[null,null,"1.安装下限离地面1.4米。"]
["10","011507001008","10kV一次结构图","个","1",{"v":30,"d":"30.00"},{"v":30,"d":"30.00"}]
[null,null,"1. 安装下限离地面1.4米。"]
[null,null,"2. 320*200 纸张打印并过塑"]
["11","011507001009","0.4kV一次结构图","个","1",{"v":30,"d":"30.00"},{"v":30,"d":"30.00"}]
[null,null,"1.安装下限离地面1.4米。"]
[null,null,"2.320*200 纸张打印并过塑"]
["12","011507001010","安全警语牌","个","1",{"v":200,"d":"200.00"},{"v":200,"d":"200.00"}]
[null,null,"1.安装下限离地面2.0米。"]
["13","011507001011","“禁止烟火”标志牌","个","1",{"v":30,"d":"30.00"},{"v":30,"d":"30.00"}]
[null,null,"1.安装下限离地面1.6米。"]
["14","011507001012","“注意通风”标志牌","个","1",{"v":30,"d":"30.00"},{"v":30,"d":"30.00"}]
[null,null,"1.安装下限离地面1.6米。"]
["15","011507001013","箱变名称标示牌","个","1",{"v":60,"d":"60.00"},{"v":60,"d":"60.00"}]
[null,null,"320*200 反光铝板丝印（户外漆）"]
["16","011507001014","箱变低压室、高压室、变压器室门牌","个","3",{"v":60,"d":"60.00"},{"v":180,"d":"180.00"}]
["注：税前项目包含除增值税以外的所有费用。"]
[{"$nulls":6},"表-14"]
["税前项目清单与计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程 ",{"$nulls":4},"第2页 共2页"]
["序号","项目编码","项目名称及项目特征\r\n描述","计量单位","工程量","金  额(元)"]
[{"$nulls":5},"单价","合 价"]
[]
[null,null,"320*200 反光铝板丝印（户外漆）"]
["17","011507001015","“接地标识”标志牌","个","1",{"v":30,"d":"30.00"},{"v":30,"d":"30.00"}]
[null,null,"80塑胶板"]
[null,null,"            合         计",{"$nulls":3},{"v":2529,"d":"2529.00"}]
{"$rows_empty":35}
["注：税前项目包含除增值税以外的所有费用。"]
[{"$nulls":6},"表-14"]

{"sheet":"表-15_规费、增值税计价表","index":8,"n_rows":73,"n_cols":5,"rows_kept":73,"merged":[[0,0,0,4],[1,0,1,3],[5,2,12,2],[16,2,22,2],[27,2,31,2],[33,0,33,4],[34,0,34,3],[36,2,38,2]],"flags":["formulas_cached_only"]}
["规费、增值税计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程",{"$nulls":3},"第1页 共2页"]
["序号","项目名称","计算基础","计算费率(%)","金额(元)"]
[null,"中国—东盟传统医药文化交流中心配电工程-安装工程",null,null,137237.46]
["1","规费","1.1+1.2+1.3",null,15367.51]
["1.1","社会保险费","∑(分部分项人工费+单价措施人工费)\r\n(48631.35+0)","29.35",{"v":14273.3,"d":"14273.30"}]
["1.1.1","养老保险费",null,"17.22",8374.32]
["1.1.2","失业保险费",null,"0.34",165.35]
["1.1.3","医疗保险费",null,"10.25",4984.71]
["1.1.4","生育保险费",null,"0.64",311.24]
["1.1.5","工伤保险费",null,"0.90",437.68]
["1.2","住房公积金",null,"1.85",899.68]
["1.3","工程排污费",null,"0.40",194.53]
["2","增值税","Σ（分部分项工程费及单价措施项目费+总价措施项目费+其他项目费+税前项目费+规费）","9.00",121869.95]
[null,"中国—东盟传统医药文化交流中心配电工程-土建工程",null,null,10606.76]
["1","规费","1.1+1.2+1.3",null,4061.43]
["1.1","社会保险费","∑(分部分项人工费+单价措施人工费)\r\n(11234.51+1039.56)","29.35",3602.44]
["1.1.1","养老保险费",null,"17.22",2113.59]
["1.1.2","失业保险费",null,"0.34",41.73]
["1.1.3","医疗保险费",null,"10.25",1258.09]
["1.1.4","生育保险费",null,"0.64",78.55]
["1.1.5","工伤保险费",null,"0.90",110.47]
["1.2","住房公积金",null,"1.85",227.07]
["1.3","工程排污费","∑(分部分项人材机+单价措施人材机)\r\n(52443.32+1492.15)","0.43",231.92]
["2","增值税","Σ（分部分项工程费及单价措施项目费+总价措施项目费+其他项目费+税前项目费+规费）","9.00",6545.33]
[null,"中国—东盟传统医药文化交流中心配电工程-市政工程",null,null,1797.67]
["1","规费","1.1+1.2+1.3",null,366.46]
["1.1","社会保险费","∑(分部分项人工费+单价措施人工费)\r\n(1159.7+0)","29.35",340.37]
["1.1.1","养老保险费",null,"17.22",{"v":199.7,"d":"199.70"}]
["1.1.2","失业保险费",null,"0.34",3.94]
["1.1.3","医疗保险费",null,"10.25",118.87]
["1.1.4","生育保险费",null,"0.64",7.42]
[{"$nulls":4},"表-15"]
["规费、增值税计价表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程",{"$nulls":3},"第2页 共2页"]
["序号","项目名称","计算基础","计算费率(%)","金额(元)"]
["1.1.5","工伤保险费","∑(分部分项人工费+单价措施人工费)\r\n(1159.7+0)","0.90",10.44]
["1.2","住房公积金",null,"1.85",21.45]
["1.3","工程排污费",null,"0.40",4.64]
["2","增值税","Σ（分部分项工程费及单价措施项目费+总价措施项目费+其他项目费+税前项目费+规费）","9.00",1431.21]
[null,"       合          计",null,null,149641.89]
{"$rows_empty":31}
[{"$nulls":4},"表-15"]

{"sheet":"主要材料及价格表(有信息价)","index":9,"n_rows":34,"n_cols":6,"rows_kept":34,"merged":[[0,0,0,5],[1,0,1,2],[1,4,1,5]],"flags":["formulas_cached_only"]}
["主要材料及价格表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程",{"$nulls":3},"第1页  共1页"]
["序号","材料编码","项目名称及规格、型号等特殊要求","单位","数量","单价（元）"]
[1,"000501000","安装人工","工日",399.377,1.13]
[2,"010103002","螺纹钢筋HRB400 10以上(综合)","t",0.577,{"v":5273,"d":"5273.00"}]
[3,"010902001","圆钢HPB300 Φ10以内(综合)","t",0.215,{"v":5527,"d":"5527.00"}]
[4,"012913002","花纹钢板 6mm","t",{"v":1.76,"d":"1.760"},{"v":5553,"d":"5553.00"}]
[5,"030183001","铁钉(综合)","kg",12.933,5.58]
[6,"031311001","电焊条（综合）","kg",56.353,{"v":6.5,"d":"6.50"}]
[7,"032116004","预埋铁件","kg",{"v":623.17,"d":"623.170"},6.02]
[8,"040102001","普通硅酸盐水泥 32.5MPa","t",2.454,507.96]
[9,"040103001","白水泥(综合)","t",0.009,823.01]
[10,"040301001","砂(综合)","",4.345,179.61]
[11,"040301004","中砂","",2.761,184.47]
[12,"040506001","砂砾石","",90.649,97.09]
[13,"041302001","多孔页岩砖 240×115×90","千块",4.094,717.48]
[14,"050102006","周转圆木(支撑)","",0.017,858.27]
[15,"050306001","周转板枋材","",0.018,1033.17]
[16,"050306002","周转枋材","",0.148,993.98]
[17,"070503006","乳白色防滑地砖 600×600×11","㎡",91.727,90.27]
[18,"130102001","调和漆(综合)","kg",9.624,10.62]
[19,"143506001","催干剂","kg",0.168,6.64]
[20,"143520001","隔离剂","kg",4.501,1.33]
[21,"143901001","乙炔气","",6.507,6.64]
[22,"143906001","氧气","",{"v":14.94,"d":"14.940"},3.98]
[23,"341101001","水","",13.878,3.34]
[24,"350103001","胶合板模板 1830×915×18","㎡",{"v":10.15,"d":"10.150"},28.32]
[25,"043104002","碎石 GD40  商品普通砼  C15","",5.989,373.79]
[26,"043104002","碎石 GD40  商品普通砼  C15","",{"v":4.09,"d":"4.090"},373.79]
[27,"043104003","碎石 GD40  商品普通砼  C20","",0.949,384.47]
[28,"043104004","碎石 GD40  商品普通砼  C25","",5.481,394.17]
[29,"140301004","国V汽油 92#","kg",0.551,8.34]
[30,"140304001","轻柴油 0#","kg",116.757,6.98]
[31,"341103001","电","kW.h",920.157,0.59]

{"sheet":"设备及价格表","index":10,"n_rows":41,"n_cols":7,"rows_kept":41,"merged":[[0,0,0,6],[1,0,1,2],[1,5,1,6]],"flags":["formulas_cached_only"]}
["设 备 及 价 格 表"]
["工程名称:中国—东盟传统医药文化交流中心配电工程",{"$nulls":4},"第1页  共1页"]
["序号","编码","设备名称、规格、型号等特殊要求","单位","数量","单价（元）","合价（元）"]
[1,"B4-0012换","干式变压器 SCB13-1000KVA","台",{"v":2,"d":"2.000"},{"v":125000,"d":"125000.00"},{"v":250000,"d":"250000.00"}]
[2,"B4-0090","高压成套配电柜 出线柜AH2","台",{"v":1,"d":"1.000"},74720.71,74720.71]
[3,"B4-0090","高压成套配电柜 出线柜AH3","台",{"v":1,"d":"1.000"},74720.71,74720.71]
[4,"B4-0090","高压成套配电柜 进线柜AH1","台",{"v":1,"d":"1.000"},76787.26,76787.26]
[5,"B4-0268","低压开关柜 出线柜1AA3","台",{"v":1,"d":"1.000"},28694.47,28694.47]
[6,"B4-0268","低压开关柜 出线柜1AA4","台",{"v":1,"d":"1.000"},{"v":29032.7,"d":"29032.70"},{"v":29032.7,"d":"29032.70"}]
[7,"B4-0268","低压开关柜 出线柜1AA5","台",{"v":1,"d":"1.000"},29435.97,29435.97]
[8,"B4-0268","低压开关柜 出线柜1AA6","台",{"v":1,"d":"1.000"},30932.92,30932.92]
[9,"B4-0268","低压开关柜 出线柜2AA4","台",{"v":1,"d":"1.000"},29592.08,29592.08]
[10,"B4-0268","低压开关柜 出线柜2AA5","台",{"v":1,"d":"1.000"},{"v":34928.5,"d":"34928.50"},{"v":34928.5,"d":"34928.50"}]
[11,"B4-0268","低压开关柜 出线柜2AA6","台",{"v":1,"d":"1.000"},31151.28,31151.28]
[12,"B4-0268","低压开关柜 进线柜1AA1","台",{"v":1,"d":"1.000"},64595.18,64595.18]
[13,"B4-0268","低压开关柜 进线柜2AA1","台",{"v":1,"d":"1.000"},64595.18,64595.18]
[14,"B4-0268","低压开关柜 联络柜2AA3","台",{"v":1,"d":"1.000"},59112.88,59112.88]
[15,"B4-0279","低压电容器柜 补偿柜1AA2","台",{"v":1,"d":"1.000"},61116.24,61116.24]
[16,"B4-0279","低压电容器柜 补偿柜2AA2","台",{"v":1,"d":"1.000"},61116.24,61116.24]
{"$rows_empty":21}
[{"$nulls":3}," ","  "," "]